## README
---README - EQUIPMENT LIST & ASSET DATABASE TEMPLATE GUIDE---
--Intent of the City of Brantford Equipment List and Asset Database Template--
This MS Excel workbook is intended to guide the construction team (Contractors, Contract Administrators, Inspectors, Owner) through the asset information collection process in a way that best serves construction phase record keeping requirements (i.e., equipment start-up proof-of-work records) while also serving future Asset Management efforts and Facility Managers during the operation and maintenance lifecycle phase of a facility. Promoting comprehensive asset information collection during the construction phase is intended to avoid duplication of efforts for Facility Managers. Equipment details are to be collected during the construction phase such that the data is transferable to asset management software.
It is recognized that asset information and organizational needs are very different during the construction phase and during the operation & maintenance phase. It is expected that the construction team will prefer to group assets by: - system, - trade - location, or by - specification divisions The populated Equipment List example offers an example of organization by system and trade. The construction team is encouraged to organize equipment lists to suite the needs of the project so that the list can be used efficiently by the team throughout construction. The Asset Management Database will build upon the asset data provided in the equipment list. For example, comprehensive Asset descriptions and Make & model information is expected to be available following construction work. It is expected that Facility Managers will tailor the grouping and categorization of these assets to suit their software import and asset management efforts.
--User Tips--
Notes regarding the intended use of each data entry field are offered in the column headings. Hover the mouse pointer over the cell to reveal data entry recommendations related to each column. Colour coding is offered to delineate fields to be populated during the construction phase by the construction team (GREY) and fields to be utilized by the asset management team (GREEN).
--Construction Phase - Equipment List Example--
An example of a populated equipment list is offered to demonstrate the expectations for data collection. This example includes equipment and assets typical of a City of Brantford Wastewater Pumping Station. Provided equipment make and model examples are not an endorsement of this equipment. It is recommended that the construction phase team refer to Contract Documents and Drawings for equipment details relevant to the specific project. References to suppliers, consultants, and contractors are offered for example and do not reflect any endorsement of said companies.
During the construction phase, the equipment list is intended to aid the construction team during equipment start-ups. It offers a systematic approach to recording start-up efforts. It should be used as a tracking form to record completed start-up efforts and to highlight pending work. It is intended to be a working document shared by the construction team; not solely as an additional close-out document submission. It can be utilized as a start-up log and be beneficial for tracking deficiencies. This database is offered in MS Excel format which is widely used by construction professionals who are typically well versed with this software. The construction team is encouraged to utilize basic MS Excel functionality to aid in tracking project progress as seen fit by the construction team. The construction team may wish to consider: - Highlighting cells during equipment start-ups to indicate where action by the team is required. - Grouping equipment and assets in a manner that suites their workflow. - Adding project specific columns (fields) tailored to the specific needs of the project (e.g. sub-contractor roles, responsibilities, task status)
The construction team should appreciate that the asset records (rows) will ultimately be imported to specialized asset management software at the discretion of the City of Brantford. Text formatting, calculation formulas, and functionality specific to MS Excel is expected to be lost during Database conversion processes. Recognize that each row used in this spreadsheet ultimately serves as a database record. Data entry during the construction phase should avoid utilizing the following MS Excel functionality: - Using multiple spreadsheet rows for a single asset (i.e., using rows as line breaks). Information within extra row may be lost during conversion to a database. Instead use a line break within the cell (Alt+Enter). - Using MS Excel functions or calculations. Only use text and numeric entries to populate a cell/field. - Using text formatting (i.e., bold, underline, italics) to distinguish between information types. Formatting is lost during data conversion. Instead use characters such as ( ) / - _ to delineate information.
--General Data Input and Spreadsheet Workflow Tips--
1) Null Cells: Fields that are not applicable to a particular asset can be indicated with '---. Note that the ' character is used in MS Excel to denote fields filled with text as opposed to a formula or a number. 2) Freeze Panes: This MS Excel tool, found in the 'View' tab, can be useful during data entry to maintain column and row identifiers on the screen while navigating the spreadsheet. 3) Wrap Text: Toggling 'Wrap text' can be used to reveal all content within a cell, or to return each record to a manageable row height. 'Wrap Text' can be found within 'Alignment' menu of the 'Home' tab.
--Operations and Maintenance Phase - Asset Database--
A populated asset database is offered as an example of the data organization utilized by asset management software and facility managers. The majority of this content can be collected directly from the Construction Phase Equipment List (i.e., copy/paste). Equipment list data not relevant to asset management software can be excluded from the Asset Database (e.g., equipment start-up records). It is expected that the spreadsheet will be modified to suite the data import requirements of the preferred DB software.
The construction team is not responsible for populating the Asset Database fields or modifying the spreadsheet for the database software import process.

## LIST & DB
---EQUIPMENT LIST AND ASSET DATABASE--- |  |  |  | Best Street WWPS, Upgrades, Contract No. XXXXXX |  | Facility Name, Project Name & Contract No. |  |  |  |  | ---
20YY-MM-DD | Revision Date |  |  | XXXX |  | Contractor & Contact Details |  |  |  |  | ---
|  |  |  | XXXX |  | Consultant/Engineer & Contact Details |  |  |  |  | ---
Construction Phase - Equipment List | [8 empty] | Equipment start-up proof-of-work | Equipment start-up proof-of-work | --- | Operations & Maintenance Phase - Asset Management Database
Con. Phase Entry No. | Con. Phase Category | Sec. No. | Equipment Description | Tag. No. Drawing or Field | Installation Location | Make, Model/Options, Supplier | Serial No. | Nominal Size, Default Settings, Power Requirements | PLC I/O, Function & Testing Observations Material/Installation Testing Observations | Asset Start-up Documentation | --- | LEVEL-1 Facility Type | LEVEL-2 Site ID | LEVEL-3 Asset Category | LEVEL-4 Parent Asset ID | LEVEL-5 Asset ID | LEVEL-6 Asset Location | LEVEL-7 Asset Sub-Class
1 | Process | XX XX XX | Pump 1 | SLP01 | Wet Well | Sulzer, XFP 201G-CB2, 8", 6 Pole 3~ 60Hz, PE 160/6 |  | 96L/s at 10.4m TDH. Amperage 4-20mA = 0-100A | 0,2,0,DI,Running - 2021-08-04 DI card I/O LED ON when pump is running and OFF when pump is not running. (Pump started and stopped from control panel). 0,2,1,DI,Control Mode - 2021-08-03 DI card I/O LED ON when in REMOTE and OFF when in LOCAL (Local/Remote switch toggled on pump control panel). 0,2,2,DI,E-Stop - 2021-08-03 DI card I/O LED normally ON when e-stop is normally pulled out and OFF when E-Stop is pushed in (E-stop button toggled at control panel). 0,2,3,DI,Overload - 2021-08-04 DI card I/O LED ON when signal wire is disconnected at pump control panel and normally OFF when re-connected. 0,2,4,DI,Temp/Leak - 2021-08-04 DI card I/O LED ON when temp or leak signal wires are disconnected at pump control panel and normally OFF when re-connected. 0,2,5,DI,Not Ready - 2021-08-04 DI card I/O LED ON when Overload, leak, or temp signals are tripped and normally OFF. 0,2,6,DI,Stat Level Relay - 2021-08-04 DI card I/O LED ON when water level is high and OFF when water level is below pump start levels. 0,2,7,DI,Stop Level Relay - Witnessed by tripping relay at Pump Backup Control Panel. 0,2,8,DI,Sort Start Fault - 2021-08-04 DI card I/O LED ON when fault is triggered from pump panel and normally OFF. 0,2,9,DI,Soft Start Bypass Mode - 2021-08-04 DI card I/O LED ON when bypass mode is activated using switch at pump control panel and normally OFF. 0,9,0,DO,Start - 2021-08-04 Pump was started via HMI 0,9,1,DO,Stop - 2021-08-04 Pump was stopped via HMI 0,13,0,AI,Amperage - 2021-08-04 4mA observed with pumps off and connectivity to PLC confirmed. Amperage at control panel (20Amps) is in agreement with amperage reported at HMI (20Amps). 2021-08-26 - Duty 1 Normal Working Level Capacity Test (1.47m START to 0.97m STOP) Observed flow was 117-113L/s through FM1 2021-10-13 Pump ran normally under PLC level control. 101 L/s through FM 1. 2021-11-08 Dual Pump Firm Capacity Testing Completed: All pump test run between 1.49m Pump 2 START setpoint and 0.99m Pump 2 STOP setpoint - Pump 1 to Forcemain 1 (112L/s) & Pump 3 to Forcemain 2 (97L/s) totaling 210L/s - Pump 1 and Pump 2 sharing Forcemain 1 operated at 140L/s. Therefore 140L/s is the current firm capacity of the station. The reported firm capacity target of 130L/s has been achieved. - Pump 2 to Forcemain 1 (110L/s) & Pump 3 to Forcemain 2 (98L/s) totaling 209L/s | 2021-02-04 Manufacturer Factory Testing Certificates 2021-08-10 Equipment Supplier Start-up Checklist | --- | WWPS | XXX | Process Equipment | Pump 1 | Pump 1 | Wet Well | Pump
2 | Process | XX XX XX | Check Valve 1 | CV01 | Pipe Room | Valmatic, 508ABFMI |  | 200mm SwingFlex w. backflow actuator | --- | 2021-09-17 Syntec Service Commission Report | --- | WWPS | XXX | Process Equipment | Pump 1 | Check Valve 1 | Pipe Room | Valve
3 | Process | XX XX XX | Knife Gate Valve - Pump 1 Riser | HV01 | Pipe Room | Trueline, F8112RSV2 |  | 200mm | 2021-09-17 Valve operator exercised through full range of motion and found to operate freely without issue. | 2021-09-17 Syntec Service Commission Report | --- | WWPS | XXX | Process Equipment | Pump 1 | Knife Gate Valve - Pump 1 Riser | Pipe Room | Valve
4 | Process | XX XX XX | Knife Gate Valve - Header | HV05 | Pipe Room | Trueline, F8112RSV2 |  | 300mm | 2021-09-17 Valve operator exercised through full range of motion and found to operate freely without issue. | 2021-09-17 Syntec Service Commission Report | --- | WWPS | XXX | Process Equipment | Process Piping | Knife Gate Valve - Header | Pipe Room | Valve
5 | Process | XX XX XX | Motorized Knife Gate Valve - FM1 | FV09 DSV01 | Pipe Room | Valve: Trueline, F8112RSV2. Actuator: Limitorque, MX-10-A1 |  | 300mm w. motorized actuator | 0,5,3,DI,Open Status 2021-10-13 LED light when open, OFF when closed 0,5,4,DI,Closed Status 2021-10-13 LED light when Closed, OFF when Open 0,5,5,DI,Control Mode 2021-10-13 LED light when in Remote, OFF when in Local. 0,11,2,DO,Open 2021-10-13 LED light when Open command is given, OFF after the 70s fail to close timer. 0,11,3,DO, 2021-10-13 LED Close w. 90s failed to close alarm (takes 70s to open) 2021-07-08 Valve local electronic control witnessed | 2021-09-17 Syntec Service Commission Report | --- | WWPS | XXX | Process Equipment | Forcemain 1 | Motorized Knife Gate Valve - FM1 | Pipe Room | Valve
6 | Process | XX XX XX | Knife Gate Valve - FM1 Drain | HV12 | Pipe Room | Trueline, F8112RSV2 |  | 100mm | 2021-08-12 Handwheel operated from fully closed to fully open | 2021-09-17 Syntec Service Commission Report | --- | WWPS | XXX | Process Equipment | Forcemain 1 | Knife Gate Valve - FM1 Drain | Pipe Room | Valve
7 | Process | XX XX XX | Combination Air Valve - FM1 | AV01 | Pipe Room | H-Tec, 986 |  | 50mm | 2021-07-20 Air valves observed to be releasing air (audible) at pump startup and stop | 2021-09-17 Syntec Service Commission Report | --- | WWPS | XXX | Process Equipment | Forcemain 1 | Combination Air Valve - FM1 | Pipe Room | Valve
8 | Process | XX XX XX | Process Piping | --- | Pipe Room & Wet Well | Custom | --- | 100mm, 200mm, 300mm | 2021-06-29 & 2021-07-01 Pressure test witnessed | 2021-06-29 GMBP Pressure Test Record 2021-07-01 GMBP Pressure Test Record 2021-07-09 WSP Weld Inspection Report 2021-07-15 Contractor Pressure Test Record | --- | WWPS | XXX | Process Equipment | Process Piping | Process Piping | Pipe Room & Wet Well | Piping
9 | Process Accessory | XX XX XX | Hoist & Monorail - Wet Well | --- | Wet Well Access Room | KITO, RCBSG005 |  | 500kg | 2022-01-11 Monorail painting witnessed 2022-01-12 Photos provided of monorail labeling | 2021-08-16 Hoist and Monorail Certification | --- | WWPS | XXX | Building Equipment | --- | Hoist & Monorail - Wet Well | Wet Well Access Room | Hoist
10 | I&C | XX XX XX | PLC Control Panel | CP001 | Control Room | Procon |  | 12" HMI video monitor screen with resolution adjusted to display HMI graphics programmed for use with 10" video monitor screens To avoid interference with High Float (which tips at approx. 1.69m as reported by primary pressure probe): START Duty 3 - 1.64m START Duty 2 - 1.49m START Duty 1 - 1.34m STOP Duty 3 - 1.14m STOP Duty 2 - 0.99m STOP Duty 1 - 0.84m 'No Flow' Alarm triggers after 20s delay on 'Pump Running' status if flow is les than 40L/s. | 0,6,11,DI,24V DC Power Supply 1 Fail Alarm - 2021-08-26 Breaker tripped and DI card LED turned OFF. 0,6,12,DI,24V DC Power Supply 2 Fail Alarm - 2021-08-26 Breaker tripped and DI card LED turned OFF. 0,7,0,DI,Power Fail - 2021-08-26 DI card I/O LED ON when PLC is Powered and OFF when breaker is tripped. 2021-08-26 Pump Control Testing: -Water level raised to point between 2nd duty and third start points (1.67m). Switched to Auto Control, and two pumps turned on as intended. A 5s delay was programmed so that pump starts are staggered. Both turned off at associated STOP setpoints. - Pumps all set to auto, water level allowed to rise till Duty 1 START setpoint. P1 started and stopped at associated Duty 1 levels. Pump duty cycled to P2 on next auto cycle for a second successful pump run 2021-11-03: Pumps observed to be cycling and starting and stopping as expected under typical influent conditions. PLC control has been in operation without fail for weeks. | 2021-05-26 Software FAT 2021-11-15 Section 4 Fifth Ave. SPS I/O Loop and PAC Panel Demonstration 2021-11-15 Section 6 Fifth Ave. SPS Software SAT 2021-11-15 Section 8 Fifth Ave. Pump Module 2021-11-15 Section 9 Fifth Ave. Valve Module 2021-11-15 Section 10 Fifth Ave. Analog Input Module | --- | WWPS | XXX | Process Equipment | --- | PLC Control Panel | Control Room | Panel
11 | I&C | XX XX XX | UPS 1 - PLC Panel | UPS01 | PLC Panel | Tripplite, SU2200RTXL2UA |  | --- | 0,5,0,DI,General Alarm - 2021-08-06 DI card I/O LED ON when test button pushed or if UPS power chord is unplugged. LED normally OFF. 0,5,1,DI,Emergency Power is ON - 2021-08-06 DI card I/O LED ON when UPS unplugged from utility power, normally OFF. 0,5,2,DI,Battery Low - 2021-08-06 DI card I/O LED ON when signal wires disconnected from back of UPS and normally OFF when re-connected. 2021-08-06 UPS successfully powered PLC when power supply was disconnected (unplugged UPS and PLC from outlet) | --- | --- | WWPS | XXX | Process Equipment | PLC Control Panel | UPS 1 - PLC Panel | PLC Panel | Panel
12 | I&C | XX XX XX | Backup Control Panel | WWL01 | Control Room | Procon |  | Backup Level Probe Control Settings: Pump 3 START 1.70m above FF with 20s delay using timer TD14 - Relay 5 = 1.40m above piezometer Pump 2 START 1.55m above FF with 10s delay using timer TD12 - Relay 3 = 1.25m above piezometer Pump 1 START 1.40m above FF with 0s delay (no timer is available) - Relay 1 = 1.10m above piezometer Pump 3 STOP 1.20m above FF with 0s delay using timer TD15 - Relay 6 = 0.90m above piezometer Pump 2 STOP 1.05m above FF with 0s delay using timer TD13 - Relay 4 = 0.75m above piezometer Pump 1 STOP 0.90m above FF with 0s delay using timer TD11 - Relay 2 = 0.60m above piezometer Backup Float Control Settings: Pump 3 START Float Timer: 40s (after High-High Float is tipped up) Pump 2 START Float Timer: 20s (after High-High Float is tipped up) Pump 1 STARTs as High-High Float is tipped up Pump 3 STOP Float Timer: 30s (after Float returns to hung position) Pump 2 STOP Float Timer: 60s (after Float returns to hung position) Pump 1 STOP Float Timer: 120s (after Float returns to hung position) | 0,2,12,DI,Backup Mode - 2021-08-04 DI card I/O LED ON when water level high, OFF when water level is low. 0,9,3,DO,USLT Backup Control Reset 2021-11-03 HMI on-screen reset button appears when backup panel is tripped into Backup level control mode. 0,9,4,DO,Float Backup Control Reset. 2021-11-03 HMI on-screen reset button appears when backup panel is tripped into Backup level control mode. 2021-08-26 Backup control is initiated at 1.69 as float tips. 2021-11-03 Backup Level Probe SAT Testing: - PLC was disabled to engage backup level probe level control - Pump START & STOP levels programmed into MultiRanger 200 - Pump START and STOP timers adjusted - Level setpoint and timer operation witnessed by allowing wet well water to raise till Float is tipper. All three pumps are witnessed to START at different times and STOP at level setpoints. After first high level cycle, single pump operation on level setpoints resumes 2021-11-03 Backup Float Control SAT Testing: - PLC was disabled & power wiring was disconnected to Backup Level Probe Transmitter to engage backup float level control - Pump START & STOP timers were adjusted to match design. - Float was tipped up by hand and held. All three pumps witnessed to start after timer delays have elapsed - Float was released and all three pumps witnessed to STOP after timer delays have elapsed 2021-12-01 Backup level control was re-tested with the reprogrammed MultiRanger 200. Pump 1, 2 & 3 Start/Stop relays triggered pump operation. | 2021-05-26 FAT 2021-11-15 Section 6 Fifth Ave. SPS Software SAT | --- | WWPS | XXX | Process Equipment | --- | Backup Control Panel | Control Room | Panel
13 | I&C | XX XX XX | Level Transmitter (Hydrostatic Probe) - Primary Level Instrument | PE LIT01 | Wet Well | Waterpilot FMX21 FMX21-CE221HGD10A+POPSZ1 |  | 4-20mA is 0.3-10.3m | 0,13,4,AI 2021-08-04 6.59mA (equating to a water depth of 3.24m with a 0-20m 4-20mA range) measured at PLC termination block is consistent with manually measured water depth of 3.28m (7.56m measured down from hatch) 4cm difference is the transmitters height above the F.F.. Drawdown measurements where in agreement with level reported at HMI. | 2021-08-19 Equipment Supplier Startup | --- | WWPS | XXX | Process Equipment | PLC Control Panel | Level Transmitter (Hydrostatic Probe) - Primary Level Instrument | Wet Well | Instrumentation
14 | I&C | XX XX XX | Float - High Level Alarm & Backup (Secondary) Pressure Probe Control | LSH01 | Wet Well | Xylem, ENM-10 | --- | Mounted 1.82m above wet well F.F. as measured by LR 2021-08-04. 6m cable. Rated for Class 1 Div 1 application. | 0,2,12,DI,Pressure Probe Backup Mode - 2021-08-26 Verified by raising water level to tip float. | --- | --- | WWPS | XXX | Process Equipment | PLC Control Panel | Float - High Level Alarm & Backup (Secondary) Pressure Probe Control | Wet Well | Instrumentation
15 | I&C | XX XX XX | Flow Meter - FM 1 | FIT 1 | Pipe Room | Endress + Hauser, Promag W 500, 5W5B3H, DN300 12" |  | 300mm 4-20mA = 0-260L/s | 0,14,6,AI - 2018-08-04 Flow was pumped through FM and Local display measurement (~120-125L/s) was in agreement with flow reported at HMI (~125L/s). 2021-07-21 Flow reported at local transmitter was recorded during pump testing and found to be in agreement with Flows measured in the wet well using a level logger and change in volume calculations. | 2021-08-04 Equipment Supplier Start-up Report | --- | WWPS | XXX | Process Equipment | PLC Control Panel | Flow Meter - FM 1 | Pipe Room | Instrumentation
16 | I&C | XX XX XX | Smoke Alarm | SD-001 (see SD6) | Control Room | Kiddle, i12010S-CA | --- | 120V, 0.8A | 0,7,3,DA,Switch N/O 2021-08-08 DI card I/O LED ON when local test button is pushed, OFF when test button is released. | --- | --- | WWPS | XXX | Building Equipment | PLC Control Panel | Smoke Alarm | Control Room | Instrumentation
17 | I&C | XX XX XX | Building temperature | TIT01 | Control Room | Greystone, TE500AD121A2 | --- | 4-20mA = 0-50 degrees C | 0,14,4,AI 2021-08-04 Temperature reported at HMI is in agreement with rooms temperature as measured with a portable instrument. | --- | --- | WWPS | XXX | Building Equipment | PLC Control Panel | Building temperature | Control Room | Instrumentation
18 | I&C | XX XX XX | Door Switches - Exterior Doors | ZS, ESW01 | Main Floor | Omron, WLMCA2-LDK13A-N | --- | --- | 0,7,4,DA, Switch N/O - 2022-03-29 Double door explosion proof door switch installed; photos provided by Contractor. | --- | --- | WWPS | XXX | Building Equipment | PLC Control Panel | Door Switches - Exterior Doors | Main Floor | Instrumentation
19 | Elec. Dist. | XX XX XX | Generator - Diesel Tank & Fuel System | DST01 | Generator | Kohler, 125/150kW | --- | 1198L (316gal) Secondary Containment Leak Float Switch Alarm: Modbus address 414000, 0 = No Leak, 1 = Leak Detected | Modbus address XXXXX Float - Diesel Tank Containment Flood - 2021-11-26 Secondary containment float communication has now been incorporated into iFix database. Float tipped and an alarm triggered by this device was witnessed at the WWTP. | --- | --- | WWPS | XXX | Process Equipment | Generator - Standby Power | Generator - Diesel Tank & Fuel System | Generator | Generator
20 | Elec. Dist. | XX XX XX | Generator - Standby Power | GEN01 | Generator | Kohler, 150REOZJF |  | 154kW, 347/600V 3~ 60Hz 185A, 70dBa Ethernet Communication Addresses: 10.199.3.14 255.255.255.0 10.199.3.254 | 0,5,6,DI, Running - 2021-08-04 DI card I/O LED ON when generator is running and OFF when generator shuts down. 0,6,7,DI, Remote - 2021-08-04 DI card I/O LED ON when generator control button toggled to REMOTE and OFF when toggled to LOCAL 0,6,5,DI, Fault Alarm - 2021-10-29 IO correction made and witnessed via faulting the generator using the emergency stop. DI card I/O LED ON for generator Fault. 0,6,14,DI, Emergency Stop - 2021-08-04 Witnessed at DI card LED 2021-08-04 Measured sound levels at construction limit (before neighbors property line) with dBa meter. 60dBa measured with generator running under low load, 54dBa measured as background noise. 2021-09-10 Ethernet card successfully pinged by Brantford SCADA group. 2021-11-03 ATS was tested by cutting power to station using main breaker. Generator was called to START successfully. ATS resumed power to station. All three pumps ran successfully using generator power. Normal power was returned to station and ATS transferred back after a delay. The generator went through the cooldown process and turned OFF automatically. | 2021-07-09 FAT Test Report 2021-08-04 Equipment Supplier Start-up Checklist and Load Bank Test 2021-09-17 Generator Inspection 2021-11-29_Generator Controller ModBus Registers | --- | WWPS | XXX | Process Equipment | --- | Generator - Standby Power | Generator | Generator
21 | Elec. Dist. | XX XX XX | Service Meter and Cabinet | --- | Control Room | Brantford Power Service Meter: 347/600V, 3~, 4 wire, Service 60-200A, S32Y30MCI Socket: Eaton Cabinet: Hammond Manufacturing |  | 3~, 600V, 200A | 2021-08-04 Operation visually witnessed while station is online and drawing load from the power Utility (meter is reporting power usage). | --- | --- | WWPS | XXX | Building Equipment | --- | Service Meter and Cabinet | Control Room | Electrical
22 | Elec. Dist. | XX XX XX | Automatic Transfer Switch | ATS01 | Control Room | Eaton, ATH3KDA30225EPC |  | 200A Time Delays: 1a Normal to Emergency Delay - 5sec, 2a Engine Start Delay - 3sec, 3a Emergency to Normal Delay - 30sec, 4a Engine Cool Down - 300sec (5min) | 0,6,3,DI,General Alarm 2021-11-03 General Alarm could not be triggered for testing. 0,6,4,DI,Normal Power is ON 2021-11-03 mixed up I/O points (6/3 and 6/4) were corrected. LED at card is light when station is in normal power and OFF when powered by Generator. 0,10,5,DO,Test 2021-11-03 ATS was tested by cutting power to station using main breaker. Generator was called to START successfully. ATS resumed power to station. All three pumps ran successfully using generator power. Normal power was returned to station and ATS transferred back after a delay. The generator went through the cooldown process and turned OFF automatically. | 2021-09-22 Equipment Supplier Start-up Checklist | --- | WWPS | XXX | Process Equipment | --- | Automatic Transfer Switch | Control Room | Electrical
23 | Elec. Dist. | XX XX XX | Master Service Breaker | --- | Control Room | Cuttler-Hammer Eaton | --- | 200A | --- | --- | --- | WWPS | XXX | Process Equipment | --- | Master Service Breaker | Control Room | Electrical
24 | Elec. Dist. | XX XX XX | Distribution Panel | --- | Control Room | Eaton | --- | 3~ 600/347V 225A 25kA | --- | --- | --- | WWPS | XXX | Building Equipment | --- | Distribution Panel | Control Room | Electrical
25 | Elec. Dist. | XX XX XX | Lighting Panel | --- | Control Room | Eaton | --- | 3~ 208/120V 225A 22kA | --- | --- | --- | WWPS | XXX | Building Equipment | --- | Lighting Panel | Control Room | Electrical
26 | Elec. Dist. | XX XX XX | Lighting | --- | Station | Un-Rated Areas: LSI Industries, LED Dome Wrap Div 2 Areas: AZZ Rig-A-Lite Products, MHD2 LED and SXPJ LED Div 1 Areas: AZZ Rig-A-Lite Products, SXPJ LED Exterior: AZZ Rig-A-Lite Products, SAFR LED | --- |  | 2021-08-04 Wet Well light functioning correctly 2021-08-04 Control Rm, Mechanical Rm & Washroom lights functioning correctly 2021-08-12 Pipe Access Rm & Pipe Rm lights functioning correctly 2021-09-09 Exterior lighting turns on when built-in photovoltaic cell is covered for 1min. 2021-10-13 Emergency Lighting was tested with local push button and turned on. | --- | --- | WWPS | XXX | Building Equipment | --- | Lighting | Station | Electrical
27 | Elec. Dist. | XX XX XX | Pump Local Disconnect Switches - Wet Well Access Room | --- | Wet Well Access Room | Eaton, DS362UX | --- |  | 2021-08-04 Power is provided to pumps when switches are engaged. | --- | --- | WWPS | XXX | Process Equipment | --- | Pump Local Disconnect Switches - Wet Well Access Room | Wet Well Access Room | Electrical
28 | HVAC | XX XX XX | Fan - Supply, FRP Wall Mount Axial Fan | FN-103 | Wet Well Access Room | Plastic air, 715 |  | 590CFM 0.1" 57dBa EXP. 1/3hp 120V 1~ 60Hz w. switch control on exterior of bldg. | 2021-07-29 Operation witnessed. Manually turned ON. | 2021-09-14 Equipment Supplier Start-up Checklist | --- | WWPS | XXX | Building Equipment | --- | Fan - Supply, FRP Wall Mount Axial Fan | Wet Well Access Room | Mechanical
29 | HVAC | XX XX XX | Damper & Actuator - Supply, Insulated Parallel Blade Wall Mount | D-103 | Wet Well Access Room | Belimo LF-120S w. ZS-260 EXP housing Alumavent 3900 series |  | 560Hx560W Insulated Parallel Blades | 2021-07-29 Operation witnessed. Manually turned ON. | 2021-09-14 Equipment Supplier Start-up Checklist | --- | WWPS | XXX | Building Equipment | Fan - Supply, FRP Wall Mount Axial Fan | Damper & Actuator - Supply, Insulated Parallel Blade Wall Mount | Wet Well Access Room | Mechanical
30 | HVAC | XX XX XX | Louver - Supply, Stormproof Wall Mount | L-103 | Wet Well Access Room | Ventex 2420 | --- | 560 X 560 Wall Penetration | 2022-01-11 Installation w. caulking has been witnessed | --- | --- | WWPS | XXX | Building Equipment | Fan - Supply, FRP Wall Mount Axial Fan | Louver Supply, Stormproof Wall Mount | Wet Well Access Room | Mechanical
31 | HVAC | XX XX XX | Heater - Unit Heater | HE-101 | Control Room | Ouellet, OHV07536AM |  | 7.5kW 3~ 600v 60Hz w. built in thermostat and summer fan | 2021-10-13 Thermostat was lowered and fan and heating coils turned on. 2021-12-01 An appropriate thermostat setting for winter was found to be level 2.5 | --- | --- | WWPS | XXX | Building Equipment | --- | Heater - Unit Heater | Control Room | Mechanical
32 | Plumbing | XX XX XX | RPZ Backflow Preventer | --- | Mechanical Room | Watts, LF909 |  | 25mm | 2021-07-16 confirmation of installation by LR | 2021-07-14 RPZ Backflow Preventer Certification | --- | WWPS | XXX | Building Equipment | --- | RPZ Backflow Preventer | Mechanical Room | Plumbing
34 | Plumbing | XX XX XX | Expansion Tank | --- | Mechanical Room | Apollo | --- | 8L (2gal) | 2021-07-16 confirmation of installation by LR | --- | --- | WWPS | XXX | Building Equipment | --- | Expansion Tank | Mechanical Room | Plumbing
35 | Plumbing | XX XX XX | Trap Primer | --- | Mechanical Room | Precession Plumbing Products, MPB-500 |  | 20mm inlet 10mm outlets | 2021-07-16 confirmation of installation by LR 2021-09-09 Primer operation witnessed when plugged into power outlet | --- | --- | WWPS | XXX | Building Equipment | --- | Trap Primer | Mechanical Room | Plumbing
36 | Plumbing | XX XX XX | Hot Water Tank | --- | Mechanical Room | Rheem-Ruud Light Duty |  | 114L (30gal), 240V 1~ | 2021-10-13 Hot water witnessed at bathroom sink | --- | --- | WWPS | XXX | Building Equipment | --- | Hot Water Tank | Mechanical Room | Plumbing
37 | Plumbing | XX XX XX | Storage Closet Utility Tub | --- | Pipe Access Room | Basin: Molded-Stone MSB2424 Faucet: Fiat (Crane) 830-AA | --- | --- | 2021-09-09 Installation witnessed | --- | --- | WWPS | XXX | Building Equipment |  | Storage Closet Utility Tub | Pipe Access Room | Plumbing
38 | Plumbing | XX XX XX | Hose Bib - Wet Well Access Room | --- | Wet Well Access Room | Custom fabrication | --- | 25mm | 2022-01-11 Hose bib, hose, and nozzle installation visually witnessed. | --- | --- | WWPS | XXX | Building Equipment |  | Hose Bib - Wet Well Access Room | Wet Well Access Room | Plumbing
39 | Struc. | XX XX XX | Generator Equipment Pad | --- | Exterior | --- | --- | --- | See material testing report | 2021-04-28 Concrete Material Testing | --- | WWPS | XXX | Building Equipment | Generator - Standby Power | Generator Equipment Pad | Exterior | Concrete
40 | Struc. | XX XX XX | Equipment Landing Block | --- | Pipe Room | --- | --- | --- | See material testing report | 2021-04-28 Concrete Material Testing | --- | WWPS | XXX | Process Equipment | --- | Equipment Landing Block | Pipe Room | Concrete
41 | Struc. | XX XX XX | Steel Beams | --- | Pipe Access Room | --- | --- | --- | See material testing report | 2021-07-05 Welding Time and Materials Checklist 2021-07-23 Weld Inspection Report by WSP | --- | WWPS | XXX | Structure | --- | Steel Beams | Pipe Access Room | Structural Steel
42 | Civil | XX XX XX | CIPP Influent Sewer Lining - Yard | --- | Site | --- | --- | --- | See material testing report | 2021-12-06 CCTV reports and video | --- | WWPS | XXX | Civil | Influent Sewer | CIPP Influent Sewer Lining - Yard | Site | Sewer
43 | Linear | XX XX XX | Asphalt Top Coat | --- | Best Street | --- | --- | --- | See material testing report | 2021-09-23 Material Testing | --- | WWPS | XXX | Civil | --- | Asphalt Top Coat | Best Street | Road
44 | Linear | XX XX XX | Asphalt Base Coat | --- | Best Street | --- | --- | --- | See material testing report | 2021-01-07 Material Testing | --- | WWPS | XXX | Civil | --- | Asphalt Base Coat | Best Street | Road
45 | Linear | XX XX XX | Sub-surface | --- | Best Street | --- | --- | --- | See material testing report | 2021-02-04 Compaction Testing | --- | WWPS | XXX | Civil | --- | Sub-surface | Best Street | Road
46 | Linear | XX XX XX | Forcemain | --- | Best Street | --- | --- | --- | See material testing report | 2021-10-06 Tracer wire Report 2020-11-13 Forcemain Pressure Test | --- | WWPS | XXX | Civil | --- | Forcemain | Best Street | Road
Note on B6: ---Field Intent--- An option field that can be used by the construction phase team to maintain table organization preferences. A sequential numbering system is recommended (i.e., 1, 2, 3, ...). The construction team may prefer a specific sequential organization while conducting start-up testing work. Subsequent database users may prefer to sort records differently. This field can be used in the future to return to the default organization preferred by the construction team.
Note on C6: ---Field Intent--- An optional field that can be used by the construction phase team to group related assets. This categorization system is to be tailored to the project and is at the discretion of the construction phase team. Categorization example: - Civil - Struc. (i.e., Structural/Architectural) - Process - Bldg. Mech. (i.e., Building Mechanical) - I&C (i.e., Instrumentation & Control) - Elec. Dist. (i.e., Electrical Distribution) - Linear
Note on D6: ---Field Intent--- Reference to the Contract Document specification Section Number describing the asset.
Note on E6: ---Field Intent--- Equipment Description/Name should clearly identify the asset and differentiate from similar equipment installed elsewhere. Exact naming is at the discretion of the construction team. The data provided in this field is expected to be used for populating the Operations & Maintenance Phase Asset Database
Note on F6: ---Field Intent-- Include any tag number identifiers used within the contract drawings or in the field.
Note on G6: ---Field Intent--- An optional field that can be used by the construction phase team to describe the physical location of the asset. Field descriptors are to be tailored to the preferences of the construction phase team. The data provided in this field is expected to be used for populating the Operations & Maintenance Phase Asset Database
Note on H6: ---Field Intent--- Product details are to be for the products installed on site. The data provided in this field is expected to be used for populating the Operations & Maintenance Phase Asset Database
Note on I6: ---Field Intent--- Record the serial number of equipment equipped with that information.
Note on J6: ---Field Intent--- Describe and characterizing size of the equipment and any key default thresholds, settings, or scaling ranges employed at time of equipment start-ups. (e.g., 300mm diameter flowmeter, 4-20mA=0-260L/s) include power requirement details if applicable (i.e., phase, voltage, amps, Watts, frequency) This systematic approach to recording equipment settings and set-up requirements can aid in streamlining equipment start-up efforts. This information included here is intended to aid in future asset replacement, equipment orders, and setup efforts.
Note on K6: ---Record Keeping Intent--- I/O Checks: Accurate recording of I/O landing points and the Contractor's verification checks are a critical component to facility start-up testing. The information recorded here can help Programmers trouble shoot instrumentation/control issues Contractors and Sub-contractors develop a proof-of-work by verifying and clearly communicating test efforts. This proof-of-work can streamline troubleshooting efforts for all parties engaged in instrument/control start-up efforts. Clearly communicating test observations can help the Contractor to minimize costs troubleshooting control/instrumentation issues. Material/Installation Testing: QA/QC verification tests and observations (Non-I/O). And inspection tests and observations verifying quality of installation (e.g. material testing results, visual witness of installation, manual operation of valves, etc.) ---Date Entry Recommendations--- For applicable Instrumentation & equipment with PLC I/O termination points. Use format: Rack,Card/Slot,Channel,Type, Description of it's function) (i.e., XX,XX,XX,DI,Alarm Name) The use of spaces is not necessary between commas which helps to reduce column width and usability of this table during start-up testing. Record Construction phase start-up tests and observations describing I/O verification. This information is kept with the I/O point info described above to ensure concise reporting. Recommended information includes: - Date of test - Description of test conducted - Status of equipment and corresponding channel status (e.g., 202X-XX-XX Float switch tipped up by hand and Ch LED ON. Float switch dropped down and ch LED OFF) ---MS Excel Tips--- Line breaks within a cell can improve readability and can be used much like a paragraph break in a document. Use Alt+Enter to create a line break. Some equipment may utilize multiple I/O points (e.g. pumps). A line break for each I/O point is recommended. The MS Excel Formula Bar (where information is typed) can be enlarged by simply hovering the mouse over its' lower extent and dragging it down.
Note on L6: Any equipment supplier start-up reports, material testing reports, etc. Include date of report, description and provider. (e.g., 20XX-XX-XX Software FAT. Panel Supply Ltd.)
Note on N6: '---Field Intent--- Type of facility.
Note on O6: ---Field Intent--- An abbreviated name for the site as prescribed by the City of Brantford. Typically three alpha characters.
Note on P6: ---Field intent--- An asset sub-category as prescribed by the City of Brantford. Valid entries include: - Process Equipment - Building Equipment - Structure - Civil
Note on Q6: ---Field intent--- An asset sub-category as prescribed by the City of Brantford describing Critical Equipment which the asset supports the operation of. For example, the following assets would support the Parent asset of Pump 1: - VFD - Pump 1 - Local disconnect - Pump 1 - Check valve - Pump 1 - Knife gate valve - Pump 1 suction - Knife gate valve - Pump 1 discharge The role of these assets are to support the function of Pump 1.
Note on R6: ---Field Intent--- Recommend copying and reviewing equipment description field from construction phase equipment list. Equipment Description/Name should clearly identify the asset and differentiate from similar equipment installed elsewhere.
Note on S6: ---Field Intent--- Recommend copying and reviewing 'Installation Location' field from construction phase equipment list. The commonly referred to name of the area that the asset is installed. Examples include: - Room names - Panel names - Areas - Building exterior - Site - Street name (assets within road right-of-way)
Note on T6: ---Field Intent--- General term used to describe the type of asset.
---DISCLAIMER - Equipment List and Asset Database Template/Example---
An example of a populated equipment list and asset database are offered to demonstrate the expectations for data collection. This example includes equipment and assets types typical of a City of Brantford Wastewater Pumping Station. Provided equipment make and model examples are not an endorsement of this equipment. It is recommended that the construction phase team refer to Contract Documents and Drawings for equipment details relevant to the specific project. References to suppliers, consultants, and contractors are offered for example only and do not reflect any endorsement of these named companies.